## Demand Calc
Water Demand Estimate and Meter Sizing Using Fixture Values
(Based on AWWA M22 Manual, Second Edition)
Project Number
Building address or number
Residential or Non-Residential
Pressure Zone at Project
| Fixture Value | Number of | Subtotal
Fixture or Appliance | (at 60 psi) | Fixtures | Fixture Value
Toilet (tank) | 4 |  | 0
Toilet (flush valve) | 35 |  | 0
Urinal (wall or stall) | 16 |  | 0
Urinal (flush valve) | 35 |  | 0
Bidet | 2 |  | 0
Shower (single head) | 2.5 |  | 0
Sink (lavatory) | 1.5 |  | 0
Kitchen Sink | 2.2 |  | 0
Utility Sink | 4 |  | 0 | Pressure Factor (See Pressure Adjustment Factors Tab
Dishwasher | 2 |  | 0 | 10
Bathtub | 8 |  | 0
Clothes Washer | 6 |  | 0
Hose connections (with 50 ft of hose)
1/2 in. | 5 |  | 0 | Residential
5/8 in. | 9 |  | 0 | Non-Residential
3/4 in. | 12 |  | 0
Miscellaneous |  |  |  | 1=Residential, 2=Non-Residential
Bedpan washers | 10 |  | 0 | 1
Drinking fountains | 2 |  | 0
Dental units | 2 |  | 0
Combined Fixture Value |  |  | 0
Residential
Demand (gpm) |  |  | 0 | 0
Non Residential
Pressure Adjustment Factor |  |  | 1.17 | 0
Total Adjusted demand (gpm) |  |  | 0
Preliminary Demand Size |  |  | 3/4" | 0.75
Velocity (fps) |  |  | 0 | 3/4"
Required Meter Size |  |  | 3/4"
Review by:
Approved by:

## Velocity (hidden)
max flow rate for respective service size at max velocity of 10 fps
Q = VA
D (ft) | D (in) | A (ft^2) | V (ft/s) | Q (cfs) | Q (gpm) | Meter Size
0.063 | 0.75 | 0.003068 | 10 | 0.031 | 13.8 | 3/4"
0.083 | 1 | 0.0054542 | 10 | 0.055 | 24.5 | 1"
0.125 | 1.5 | 0.012272 | 10 | 0.123 | 55.1 | 1-1/2"
0.167 | 2 | 0.021817 | 10 | 0.218 | 97.9 | 2"
0.25 | 3 | 0.049087 | 10 | 0.491 | 220.3 | 3"
|  | Q (gpm) = | 0 |  | A (in^2) = | 0.44156 | 0.75
|  | Q (cfs) = | 0 |  | A (ft^2) = | 0.0030664
Velocity (fps) =
Demand (Q gpm) =
|  | Meter Size (Pipe Size in) = | #DIV/0! | = | #DIV/0!

## Residential Curve (hidden)
Residential |  |  | Actual Residential
Ax +Bx^2 + C = y
A | B | C
0.071619 | -2.6972e-05 | 17
x | y |  | x | y |  | Squared Error
18 | 18.2804 |  | 18 | 18 |  | 0.078631
40 | 19.8216 |  | 40 | 20 |  | 0.031818
115 | 24.8795 |  | 115 | 25 |  | 0.014511
205 | 30.5485 |  | 205 | 30 |  | 0.30086
283 | 35.1082 |  | 283 | 35 |  | 0.011703
380 | 40.3207 |  | 380 | 40 |  | 0.10285
460 | 44.2378 |  | 460 | 45 |  | 0.58101
580 | 49.466 |  | 580 | 50 |  | 0.28511
723 | 54.682 |  | 723 | 55 |  | 0.1011
988 | 61.4319 |  | 988 | 60 |  | 2.0503
1250 | 64.3812 |  | 1250 | 65 |  | 0.38288
[5 empty] | Total | 3.9407

## Non-Residential Curve (hidden)
Non-Residential |  |  | Actual Non-Residential
Ax +Bx^2 + C = y
A | B | C
0.11947 | -3.6236e-05 | 38
x | y |  | x | y |  | Squared Error
25 | 40.964 |  | 25 | 40 |  | 0.92936
60 | 45.0376 |  | 60 | 45 |  | 0.0014122
105 | 50.1445 |  | 105 | 50 |  | 0.020894
148 | 54.8874 |  | 148 | 55 |  | 0.012674
190 | 59.3906 |  | 190 | 60 |  | 0.37132
240 | 64.5849 |  | 240 | 65 |  | 0.17229
289 | 69.4995 |  | 289 | 70 |  | 0.25047
338 | 74.2401 |  | 338 | 75 |  | 0.57738
400 | 79.9891 |  | 400 | 80 |  | 0.0001191
452 | 84.596 |  | 452 | 85 |  | 0.16324
518 | 90.161 |  | 518 | 90 |  | 0.025913
578 | 94.9461 |  | 578 | 95 |  | 0.0029033
652 | 100.4885 |  | 652 | 100 |  | 0.23861
723 | 105.4331 |  | 723 | 105 |  | 0.18758
805 | 110.6892 |  | 805 | 110 |  | 0.47496
883 | 115.2366 |  | 883 | 115 |  | 0.05599
978 | 120.1796 |  | 978 | 120 |  | 0.032272
1083 | 124.882 |  | 1083 | 125 |  | 0.013918
1207 | 129.4064 |  | 1207 | 130 |  | 0.35241
[5 empty] | Total | 3.8837

## Pressure Adjustment Factors (hidden)
Pulldown Menu | Working Pressure | Pressure Adjustment
Number | at Meter Discharge | Factor
1 | 35 | 0.74
2 | 40 | 0.8
3 | 45 | 0.85
4 | 50 | 0.9
5 | 55 | 0.95
6 | 60 | 1
7 | 65 | 1.05
8 | 70 | 1.09
9 | 75 | 1.13
10 | 80 | 1.17
11 | 85 | 1.21
12 | 90 | 1.25
13 | 95 | 1.3
14 | 100 | 1.34
15 | 105 | 1.38
16 | 110 | 1.42
17 | 115 | 1.46
18 | 120 | 1.5
19 | 125 | 1.54
20 | 130 | 1.59

## Meter Size (hidden)
Design
Meter |  | Capacity
Size |  | (gpm)
3/4" | 0.75 | 24
1" | 1 | 40
1 1/2" | 1.5 | 80
2" | 2 | 128
3" | 3 | 250
4" | 4 | 400
6" | 6 | 800